## Slide 1
INVESTIGATION OF INERTIAL SUPPORT LIMITS IN WIND TURBINES AND THE EFFECTS ON THE POWER SYSTEM STABILITY
Erencan DUYMAZ
Supervisor: Assist. Prof. Dr. Ozan KEYSAN
Friday, January 18th, 2019
Thesis Defence
For
The Degree of Master of Science

## Slide 2: Agenda
  Problem Definition: Renewable Energy Problems
  Grid Inertia, Frequency and Inertial Support
  Wind Turbine Modelling
  Fast Inertial Support
  Synthetic Inertia Support
  Economical Perspective

## Slide 3: Renewable Energy Problems
  Benefits:
    Renewable Energy Reduces:
      Fossil Fuel Usage
      CO2 Emission
  Challanges:
    Operational Problems:
    Grid Inertia

## Slide 4: Synchronous Generator
: Mechanical Input Torque
: Electromechanical Output Torque
Notes: Synchronous generators produces torque only in synchronous speed.
When they are sycnhronized to grid frequency, Tm=Te

## Slide 5: Swing Equation
Notes: Swing Equation is important for power system frequency stability and investigated the relation between speed and the power.

## Slide 6: Frequency
Frequency Regulating Mechanisms in Grid:
Primary Frequency Control
Secondary Control
Tertiary Frequency Control
Notes: When all generators in the grid is considered as a single generator,

## Slide 7: Frequeny Disturbance
Inertial Support
Frequency decline is arrested by Inertial Support and Primary Frequency Controllers
Higher Grid Inertia  Lower RoCoF

## Slide 8: Renewable Energy Problems
The inertia in the wind turbine is not reflected to grid.
The increase in the share of RE causes the risk of frequency stability.
Existing structure decreases grid inertia!

## Slide 9: Swing Equation
Notes: Synchronous generators produces torque only in synchronous speed. Sychnous

## Slide 10: Frequency

## Slide 11: Frequency

## Slide 12: Frequeny Disturbance
Inertial Support

## Slide 13: Wind Turbine Modelling
Notes: Figure shows the modelling for the PMSG wind turbine that is connected to grid with FSPC. There are two converters in this type of the converter with different responsibilities. The one connected between DC-bus and grid is called Grid Side Converter and it is responsible for maintaining a constant DC-bus voltage and adjusting the reactive power that is injected to grid. The converter in between DC bus and PMSG is called Machine Side Controller. It is adjusts the generator and turbine speed to MPPT speed by controlling its output torque. When the output torque hits the limit, the speed cannot be regulated and exceeds the maximum allowable speeds. This is why Pitch angle controller is utilized. By increasing the pitch angle of the turbine, the aerodynamic power and aerodynamic torque is decreased. In this way, turbine speed is kept in the maximum in high speeds.

## Slide 14: Wind Turbine Modelling

## Slide 15: Fast Inertia Support

## Slide 16: Effects on the Turkish Electricity System
Notes: In order to investigate the effect of the synthetic inertia implementation, the 2018 generation data has been used. In the figure, black line shows the variation of the generation meanwhile the red line shows the generation of wind + solar energy. The maximum generation occured in the 3th of August with a generation of 46GW. The minimum of the load has occured in a religious holiday on the 16th of July with a generation of 18GW.
The generation data can be used to roughly estimate the aggregated inertia constant in the grid.
As stated before, the effective inertia contribution from wind and solar systems are zero. Moreover, the inertia constants of the synchronous generators vary between 2-9. By using zero inertia constant for wind and solar, H=5s for others, the effective inertia constant can be calculated.s

## Slide 17: Effects on the Turkish Electricity System
The aggregated inertia constant can be improved with synthetic inertia implementation.
Notes: The effective aggregated inertia in the system is shown in the graph. Notice that the inertia constant decreases down to 3.97s when the 20% of the generation is supplied from wind and solar in 26/09/2019 on 3 pm.
It is possible to improve the effective inertia constant of the grid with synthetic inertia implementation. Note that the 54% of the installed wind energy systems in Turkey has FSPC. By assuming that 54% of wind energy production is obtained from these wind turbines and implementin inertia constant of h=10s, the improvement can be calculated.
When the method is implemented on the wind turbines with FSPCs,

## Slide 18: Effects on the Turkish Electricity System
Date | 26/09/2018
Hour | 03:00:00
Total Generation (MW) | 27495
Wind (FSPC) (MW) | 3045
Wind (Other) (MW) | 2594
Solar (MW) | 0
Other (MW) | 21773
Existing Case | H=3.97s
With Synthetic Inertia (H=10) | H=5.08s
Notes: The existing inertia constant and inertia constant with synthetic inertia is shown in the figure. Notice that the inertia constant is above the H=5s. That means the wind turbines can compensate the decrease in the inertia constant caused by them and also caused by solar energy. Note that the inertia constant is maximum where the existings case inertia constant is minimum.

## Slide 19: Economical Perspective

## Slide 20: Economical Perspective
Net additional energy is zero! (There exists losses due to deviation from MPPT, inside the gearbox, converter etc.)
Let us only pay for increased period (neglect the decrease):
A single support profit: $0.276 vs Daily Generation=$1679
Not possible with additional energy!
Inertial support might be paid with incentives.
Incentives will end at the end of 2020 for the new generation renewable energy systems. A new incentive might be inertial support from renewable energy systems!

## Slide 21: References